## BoQ
Transformer & Electrical Package
ELECTRICAL WORKS
MHAC, H-8 Building, Islamabad
BOQ OF ELECTRICAL WORKS
Item No. | Description | Unit | Qty | Unit Cost | Total Cost
A | Transformers
Indoor / Outdoor type oil immerrsed / dry type transformer manufactured according to BS-171, IEC-60076, specifications and consisting of filling device, drain plug, oil level indicator, lifting hooks, bi-directional roller wheels, H.V. & L.V. porcelain bushings, off load voltage tap changer, 2 earthing terminals, oil conservator and silica gel breather, imported double float buckholz relay, pressure relief vent, dial type thermometer with alarm & trip contacts, rated Voltage 11000 / 415 / 230 Volts, suitable for an ambient temperature of 50°C, winding temperature 55°C and oil temperature 50°C, impedance 6.25% or as specified by IEC, system earth: Delta-Y, neutral solidly earthed (DYN-11) and all necessary accessories / materials, complete in all respects, including submission of technical data sheet. WAPDA / IESCO approved.
A.01 | 630kVA Transformer, 11kV to 415V, Dyn-11, ONAN / AF / AN (As Available) | Nos. | 1
B | Cables
Supply, Installation, Testing and Comissioning of HT cables complying to IEC 60364-5-52. Recommended make of Pakistan Cables, Fast Cables, Newage. From Main HT Line to Transformer.
B.01 | 35mm, 3-Core | Mtr. | 20
Supply, Installation, Testing and Comissioning of cables with Cu/PVC/PVC insulation, non-armoured copper conductor with 600 / 1000 V grade installed in conduits / trenches / trays / ladders including all auxiliaries with complying to IEC 60364-5-52. • Cable laying to be inside PVC D-Class pipe from Transformer to LT Panel. Recommended make of Pakistan Cables, Fast Cables, Newage. From Transformer to Main LT Panel through designated route.
B.02 | 240mm, 1-Core, 2 Runs Per Phase, 3 Phase + Neutral | Mtr. | 800
C | Main LT Panel:
Supply, Installation, Testing and Comissioning of Form-4B Type-6 Main LT Panel with following specifications: Complying to IEC 61439-2. 2mm sheet thickness. IP54 indoor type, floor mounted. Totally enclosed assembly with cubicle based construction. Hinged doors, handles including all auxiliaries. All Busbar with ampacity not less than 1 A / mm2. Main Busbar equivalent to or higher to the rating of the Main Incomer. Neutral Busbar 50% of the main. Earth Busbar 25% of the main. Copper conductivity not less than 95%. Complete with cable terminal block, wiring from breakers, cable glands, digital energy analyzer with RS-485 communication, including all electro-mechanical interlocking where necessary. Including system load flow, short circuit, zone-selectivity and arc flash analysis study on approved software package i.e. Etap, E-Design (ABB), Ecodial (Schneider), Simaris (Siemens) or any other corresponding to the brand of switchgear offered by the vendor. • All ACB's to have motor mechanism inlcuding SOR, SCR, UVR, Operation Counter, LSIG trip unit with built-in display, with RS-485 communication. • All circuit breakers of 800AF and above to be ACB type. • All circuit breaker of rating less than 800AF to be MCCB type. • All MCCB's to be have LSI trip unit. • All circuit breakers to be provided with dedicated energy analyzers with RS-485 communication capability separately mounted in an enclosure to the far left / far right side of the LT Panel. • Main Incomer from Transformer and Diesel Generator to be Electrical & Mechanical (E&M) Interlocked. • The Interlocking to be supplemented with an Electronic Controller for Auto-Transfer System of a reputed brand prefarably ComAp, Woodward, Deepsea, Dief, Sices. • Incoming (Transformer & Generator) cable termination from panel bottom side. • Outgoing cable termination from panel top side. • All accessories including cable glands, thimbles, cable ties etc. necessary for cable termination to be included in the LT Panel offer. • Recommended make of switchgear to be ABB, Schneider.
C.01 | Main LT Panel | Nos. | 1
Incomer: 1000AT / 1000AF, ACB, 3P from Transformer (1 No.) Incomer: 1000AT / 1000AF, ACB, 3P from Generator (1 No.) Outgoing: 630AT / 630AF, MCCB, 3P (1 No.) (For Capacitor Bank, PFI / PFC Panel) 250AT / 250AF, MCCB, 3P (4 No.) 160AT / 160AF, MCCB, 3P (4 No.) 100AT / 160AF, MCCB, 3P (6 No.) 63AT / 160AF, MCCB, 3P (16 No.)
D | Automatic Power Factor Improvement Plant (PFIP)
Supply, Installation, Testing and Comissioning of PFI panel with following specifications: Complying to IEC 61439-2. 2mm sheet thickness. IP54 indoor type, floor mounted. Totally enclosed assembly with cubicle based construction. Hinged doors, handles including all auxiliaries. All Busbar with ampacity not less than 1 A / mm2. Main Busbar equivalent to or higher to the rating of the Main Incomer. Neutral Busbar 50% of the main. Earth Busbar 25% of the main. Copper conductivity not less than 95%. Complete with cable terminal block, wiring from breakers, cable glands, digital energy analyzer with RS-485 communication. • All steps to have MCCB protection. No HRC fuse acceptable. • All contactors to have damping resistors. • 12 step PF controller with built-in RS-485 communication capability • All steps to include complete manual and auto configuration switches.
D.01 | Power Factor Improvement Panel, 225kVAR Capacity having step configuration as follows: 12.5kVAR x 2 Steps 25kVAR x 4 Steps 50kVAR x 2 Steps | Nos. | 1
E | Earthing
Supply, Installation, Testing and Comissioning of earthing pits with arrestor, copper conductor, borewell, earthing rod with all accessories included (where applicable).
E.01 | Earth Pit (For Transformer Neutral) with all cabling included as follows: • Resistance less than 0.5 Ohm. • 70mm Sq. Copper Conductor • ECP Box | Job | 1
E.02 | Earth Pit (For Transformer Body) with all cabling included as follows: • Resistance less than 0.5 Ohm. • 70mm Sq. Copper Conductor • ECP Box | Job | 1
E.03 | Earth Pit (For LT Panel) with all cabling included as follows: • Resistance less than 0.5 Ohm. • 70mm Sq. Copper Conductor • ECP Box | Job | 1
E.04 | Earth Pit (For Lighting Protection) with all cabling included as follows: • Resistance less than 0.5 Ohm. • 70mm Sq. Copper Conductor • 25x4 Copper Strip • Copper Rod with ball • Copper Spikes • ECP Box | Job | 1
Total Amount