## Sheet1
New Premises of MHAC Lahore
BILL OF QUANTITY
FOR
250 KVA Generator, ATS Panel, Power Cable, Main DB, Earthing and Generator bed
S NO | DESCRIPTION | UNIT | QTY | RATE(Rs) | AMOUNT(Rs)
E-01 | GENERATOR
| Supply, installation, testing and commissioning of 250 kVA, 3 phase, 4 wire, 50 Hz diesel generator set imported ( Other then local or China assembled ) complete in all respect including heavy duty frame base, batteries and anti-vibration mount, loading , unloading transportation, with following specifications: Engine: 4-stroke, 6 cylinders, with electronic governor, 1500 RPM, water-cooled, Diesel engine. Main Alternator: Brushless self-excited, series star connection, single bearing, revolving field, 4 pole 12 leads, with frequency of 50Hz, Power factor 0.8 legging, Voltage regulation ±1%, H class insulation and with efficiency of 93.3% Control Panel: with LED/LCD display and following parameters: Protection Features: • Over/under voltage • Over/under frequency • Overcurrent • Engine over/under speed • High coolant temperature • Low oil pressure • Battery failure • Emergency stop, automatic shutdown on fault conditions (overload, low oil pressure, high coolant temperature) • Remote start option. Parameters Monitored: • Voltage (V) • Current (A) • Frequency (Hz) • Power (kW, kVA,) • Engine Run time • Engine speed (RPM) • Fuel level • Oil pressure • Coolant temperature • Battery voltage Fuel Tank: Built in fuel tank with standard fuel capacity and fuel indication gauge. Canopy: Construction and Materials • Material: Galvanized steel or powder-coated steel for durability and corrosion resistance. • Thickness: 1.6 mm to 2.0 mm for panels and doors. • Frame: Heavy-duty, welded steel frame for structural integrity. • Design Features • Weatherproofing: Designed to withstand harsh weather conditions, including rain, wind, and UV exposure. • Sound Attenuation: Soundproofing material (e.g., acoustic foam) lining the interior to reduce noise levels. • Noise Level: Capable of reducing noise to 75 dB(A) at 7 meters. • Ventilation and Cooling • Air Inlet Louvres: Strategically placed to ensure adequate airflow to the engine and alternator. • Exhaust System: Integrated or provisioned for proper exhaust routing and emission dispersal. • Cooling: Adequate space and venting to facilitate the generator’s cooling system. • Access and Maintenance • Doors: Lockable doors on both sides for easy access to the engine, alternator, and control panel. • Hinges: Heavy-duty, rust-resistant hinges for long-term use. • Handles: Ergonomic, corrosion-resistant handles. • Mounting and Installation • Base Frame: Integrated with anti-vibration mounts to reduce operational vibration and noise. • Lifting Hooks: Certified lifting hooks or eyes for safe transportation and installation. • Electrical Provisions • Cable Entry: Weatherproof cable entry points for power and control wiring. • Finish • Coating: Powder-coated or painted with weather-resistant paint. • Color: Standard color white or grey. • Compliance and Standards • Fire Resistance: Materials should comply with fire safety standards to ensure safety. • Security: Lockable doors and panels for enhanced security against theft or tampering. • Signage: Clear labeling and safety signage as per regulations. | Each | 1
E-02 | ATS PANEL FOR 250KVA GENERATOR
| Providing, Installation, Testing & Commissioning of 440 Volts, 3-Phase , 4-pole ATS Panel, with Motorized Change over Swithch ( insted of Megnatic contactors) and protected with phase sequence relay. Panel box must be duly powder coated, and water proof, battery charger with auto cut off function, auxiliary relays, volt rmeter, selector switch, to monitor each phase voltage, indication lights, for generator, wapda and load, timers, control cable, including wiring, termination , thimbles etc, complete in all respect as approved by the Engineer. | Nos | 1
4 CORE COPPER POWER CABLE
| Supply and instalation of good quality (approved by the Engineer) 4 core 240 mm copper pwer cable from generator to ATS pannel and from ATS Panel to main DB. (Payment based on Measurement, as per actual) | Mtrs | 50
E-04 | ERTHING PITT FOR GENERATORS
| Constructing, erecting, earthing pit including cost of excavation and back filling of the earth pit upto 3500 to 4500mm depth and including electrode comprising of one 16 mm dia earth electrode rod of 3600 mm long with loop conductor as bare copper conductor 70 mm2 to be drawn in 40mm dia uPVC sleeves from copper plate (50x200 mm) to earth terminal point or adjacent earthing pit or direct to equipment (as directed by Engineer-in-Charge) complete with thimbles, brass nuts and bolts for fastening earth conductor and also including constructing inspection pit 450mm x 450mm x 200mm with RCC cover complete with all necessary materials complete in all respects as per detail shown in the drawing with final testing and commissioning including the cost of earthing leads. Earth Loop Conductor. Providing and laying earth loop conductor complete with fixing, arrangement from one earthing pit to another earthing pit with lugs and thimbles, washers and Bare copper conductor 16mm sq.Earthin value must be less then or equal to 0.5 Ω | Job | 1
E-05 | GENERATOR BED
| Construction of bed of 6 inches PCC 1:4:8 over 6 inches RCC 1:1.5:3 including MS steel bar No. 3 @ 5'' c/c and according to the size of generator, complete with all respect and as per direction of Engineer In charge | Job | 3
E-06 | Shifting and installation of GenSet from Gulberg Office, Lahore to MHAC new Site including carriage loading, unloading, connections, testing and commissioning, complete with all respect and as per direction of Engineer in charge | Job | 2
| Total | (Rs.) |  |  | 0