## Table 1
BoQ of 10 KW Solar System-GGPS # 02 Bara Line-Peshawar
|  | Description of Work | Unit | Quantity | Unit Rate | Total Amount
S,No | MRS 2022 (Item Code) | Solar System of GGPS#2 Bara Line Peshawar
General Specification of Solar system. The system is designed to cover the all loads in the School Buildings. The system will be grid interactive connected system, which will allow for many power sources options. The system will import from the grid when loads are being more than the generated from PV and supply surplus electricity to the batteries when PV generates more than the loads, the batteries can be charged from Grid if PV output is not enough for loads and batteries. • Contractor shall submit shop drawings of all Electrical ,civil and solar photovoltaic complete system Works,including a single line diagram showing all the components of the PV system, DC and AC distribution boards, PV panels lay out and backup systems and wires cross section for all the system to be approved by the Engineer before executing the work. As well as the catalogs of each component showing the requested specifications stated at the bill of quantity. • All junction boxes and DBs will be lockable type. • Upon completion of the installation, the contractor shall organize an on site training program involving nominated employer's staff. Such a program shall be carried out during the commissioning phase. The cost of the training shall be deemed to have been included in the tendered rates. • The price includes all builders’ Works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites and tronsputation cost, asper instruction of Engineer Inchrage.
1 | 6-01-d-01 | Supply and Erection of Solar PV Module (Solar Panel) Mono-crystalline A-Grade (per Watt) a (As per Approved Specifications of KP Govt for solar installation and allied equipments.(Attached) | Per Watts | 10000
2 | 26-01-i-03-a | Supply and Erection of GRID TIE INVERTER (ON-Grid Inverter 0-10 KW ) (As per approved Specification of KP Govt/C&W approved documents for Solar).Recommended Brands inverex,Tesla, OR Equivalent. | Per watt | 10000
3 | NSI | Battery Bank: Supply and Erection of Lithium ion LiFeP04 battery 100 Ah,48 volts with 05 Years Warranty as per specification of KP Govt. ments applicable on site ,the allowable voltage drop must be less than 3%. | No. | 4
4 | NSI | PANEL MOUNTING & STRUCTURE: The panel mounting and structure should be made of hot dipped (80 microns Average) Galvanized steel of minimum thickness of 12 SWG / 2.64 mm Channel / Pipe or 8 SWG 4.06 mm Angle (Profile of channel and Sketch Attached in Speficition). sketch of the mounting frame (As per Actual Site Requirements) showing dimensions of the frame parts should be provided at the time of supply. The prices of nuts bolts etc. it will be included in quoted rates. | L.S | 1
5 | 17-10-a-01 | PCC 1:2:4 for PV Mounting Legs as per requirement and instruction of Engineer Inchrage. | CFt | 101.25
6 | 17-10-a-01 | Supplying and installation of Combiner box including required AC Fuses, Circuit brakers, Auto changeover switch and DC Fuses//Breakers (63 AMP at least or as per requirement) from input - out put side of power supply as per instruction of engineer incharge,Complete with all respect. | Job | 1
7 | NSI | Supply and Erection of Monitoring meters DC Voltmeter (Solar panel/battery) AC Voltmeter (wapda/Load) | Job | 1
8 | NSI | Supplying and installation of a complete earth system 3 meter copper rod , manhole with iron cover, cooper lightening arrestor, earth joints, clamps, GI Pipe, and 16 mm2 flexible copper cable from the structure to the copper rod, all necessary copper wires to connect arrays and modules in one loop for earthen. All precaution to have the resistance < 2Ω. All works and materials must be according specifications and supervisor instructions and approval. | Job | 1
9 | NSI | Supply ,install and connect all DC cables appropriately sized (10mm or as per need) in accordance with the installation requirements and to connect the inverter with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors and workmanship needed to have a complete job, the allowable voltage drop for DC cables between inverter and PV system less than 3%. Fast ,Pakistan cable or Equivalent as per Specification of KP Govt for Solar system. | RFT | 300
10 | NSI | Supply ,install and connect all AC cables appropriately sized (10mm or as per need) in accordance with the installation requirements and to connect the inverter with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors and workmanship needed to have a complete job, the allowable voltage drop for DC cables between inverter and PV system less than 3%.Pakistan cable or Equivalent as per Specification of KP Govt for Solar system. | RFT | 400
11 | NSI | Supply and Erection of BOX / STAND for Batteries SHS Inverter & Charge Controller the batteries should be housed in a vented compartment/stand that prevents users from coming in contact with battery terminals. This compartment/stand should be strong enough to accommodate the weight of the battery. b. A mechanism to prevent opening and entry of the battery should be provided. c. This compartment should be manufactured of mild steel of at least 18 SWG. d. The compartment should be powder coated paint. e. The entire enclosure/stand must be constructed to last at least twenty yearrs without maintenance and should be protected against corrosion. The enclosureks ot.lict have a clean and neat appearance. Battery Box /stand should be installed at a plac42% -accordance with user's preference and lockable | Job | 1
Total Estimated Cost of Solar System in PKRS=