## CIVILWORKS
Rehabilitation works for IOM-MHD Islamabad Office at Sector H/8, Islamabad
Ref # RFQ/PAK/May/2023 /040
BoQ’s for Civil Works
Item No. | Description | Qty | Unit | Rate (Rs) | Amount (Rs)
C1 | R.C.C 4000 Psi | 391.08 | Cft
Providing, and laying reinforced cement concrete using screened crushed stone graded aggregate 3/4 inch (19 mm) and down gauge having a minimum cylinder crushing strength of 4000 lbs. per sq. inch at 28 days with including form work and its removal, compacting, levelling, and curing etc. complete in all respects but excluding the cost of reinforcement. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge.
C2 | Wall
Brick Work
Providing and laying first class solid good finishing surface burnt brick masonry, set in cement morter 1:6 for brick work in straight or curved wall 4.5" thick including scaffolding and its removal, raking, out joints, and curing etc, complete in all respect
| Basement | 215.5013 | Cft
| Ground Floor | 659.1769 | Cft
| First Floor | 1095.0463 | Cft
C3 | Mumty Fabrication
| Providing & Installing 2X Prefabricated structures 20F X 10F to be installed as per drawing. Both structures to be provided with finished flooring, ceiling, doors & windows etc. 2X 2 tonne AC to be installed in each structure. Commercial grade, 3 ply (3-5mm preferably ) Fibre Shed top 36F (L), 12F (W) and 6F Deep to be installed on 16 Gauge SS Pipes. Both side ends to be covered with same fibre and fibre partitions within the structures. Front open and back sides to be left open for at least 2feet for ventilation including shelf space for placing of tissue paper, rack etc inside each cabin. | 1 | Job
C4 | Plaster
Providing 13mm thick cement plaster (1:4) on wall. including making edges, corners, curing, stagging, and scaffolding etc. Including cost of Providing and fixing chicken mesh with nails over all joints of walls with columns, beams, and footing bed. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge
| Basement | 2172.6416 | Sft
| Ground Floor | 119.1251 | Sft
| First Floor | 157.7402 | Sft
| Mumty | 150 | Sft
C5 | Plastic Emulsion
Painting with (ICI/Burger/Nippon etc) Dulux plastic emulsion paint V I P of approved shade two coats over primer and including the cost of one priming coat complete over plastered surface at any height in floor.
| Basement | 2172.6416 | Sft
| Ground Floor | 119.1251 | Sft
| First Floor | 157.7402 | Sft
| Mumty | 150 | Sft
C6 | Reinforment
| Providing and laying M S Deformed grade 60 Steel reinforcement bars with minimum yield stress of 60,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, overlaps complete in all kinds of R.C.C work. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 0.95 | Ton
C7 | Aluminium Windows
| Providing and fixing fully glazed double leaf hung dulux model aluminium windows and ventilators of approved make A.C.P/Pak cable including 6mm thick best quality tinted blue colour glass 12mm thick on glass shatter Resistance film SRF 12 mils (.012 inch) Thickness Place with adessive material and aluminium fittings including wire mesh, lugs cutting holes and making good damages to wall etc. complete. Ornamented balustrade outside windows in entrance lobby and stores as per drawings floor or as directed by Engineer Incharge. | 574 | Sft
C8 | Tempered Glass
i) | Providing and fixing of 12 mm tempered glass Door in partition walls including aluminium frames of required section, frosting paper all necessary fittings i.e., locks, handles, hinges, netting and cutting in all floors. Handle of superior quality, viewing glass made of polycarbonate or 10 mm thick tempered glass, hinges made of SS304 and chemical resistant especially to Hypochlorite solution, alcohol, etc., flange to seal pass-box and sandwich panel, etc complete in all respects as specified. The height & width of door placed at changing room required additional glass partition to make it higher and can be used when required. i.e., shifting of heighted instruments. This can be achieved with additional partition and can be removed when required with aluminium frame.
| Basement | 24.5 | Sft
| Ground Floor | 187.425 | Sft
| First Floor | 62.475 | Sft
ii) | Providing and fixing of 12 mm tempered glass partition in partition walls inclduing aluminium frames of required section, frosting paper all necessary fittings i.e. locks, handles, hinges, netting and cutting in all floors etc complete in all respects as specified
| Basement | 95 | Sft
| Ground Floor | 119.1251 | Sft
| First Floor | 227.115 | Sft
C9 | Wood Work
i) | Providing and fixing 2-1/2" best thick quality deodar wood Frame partition on the side Ply as per drawings fittings to be fixed etc. complete but excluding cost of kick plates, door lock and sliding bolts. complete as specified and as directed by Engineer Incharge.
| Basement | 988.47 | Sft
| Ground Floor | 3240.762 | Sft
| First Floor | 561.75 | Sft
ii) | Providing and fixing 24" x 18" mrror of imported Belgium glass or equivalent as approved, with deodar wood frame complete with 4 mm commercial plywood backing fixed to wall with spacers using C.P. screw 2" long complete. (Deodar wood frame size 1-1/4" x 3/4") including painting/polishing complete. | 120 | Sft
iii) | Providing and fixing (45mm) Thick Hollow Flush doors and windows with commercial ply (3 ply) on both faces of deodar wood shutter frame 1¼" (30 mm) thick and partal wood braces at about 3" (75 mm) apart and deodar wood lipping 1½"x3/8" (40 mmx10 mm) fixed with Wooden chowkat (frame). including chromium plated fittings, etc. Hatch doors complete in all respects (including sliding bolt or lock):
iv) | Door finishes shall be chemical resistant, anti-fungal and anti-bacterial properties. (1.2mm thick GPSP sheet suitable to fix on 60 mm thick wall panel with provisions for double glazing glass for all door and hardware like push plates and handle on both side, lock and key, etc) PUF Panels will be with GPSP Sheets, epoxy painted on both sides and PUF insulation of minimum 38-40 kg/m3. Concealed hardware for fixing of door frames, TS-71 door closure, SS Door handle, SS ball bearing butt hinges, concealed tower bolt for the double door, both sides lock and key arrangement. Suitable neoprene “Y seal” type gaskets may be used between the door jam and door stop
| Basement | 205.8 | Sft
| Ground Floor | 253.575 | Sft
| First Floor | 540.225 | Sft
C10 | Aluminium
i) | Providing and fixing all types of partly fixed and partly openable glazed anodised bronze colour Aluminium doors, using delux section of M/s Al-Cop or Pakistan Cables, having chowkat frame of size 40 x 100 mm (1½" x 4") and leaf frame of 60x40mm (2½"x1½") wide sections including the cost of ¼" (5 mm) thick imported Green tinted glass with aluminium triangular gola and rubber gasket to support the glass and single leaf edging, using approved standard fittings, locks, 3" (75 mm) wide long handles, Hatch doors etc., and hardware any required as approved by the engineer in-charge
| Basement | 159.8625 | Sft
| Ground Floor | 51.45 | Sft
| First Floor | 338.1 | Sft
ii) | Providing and fixing fully glazed double leaf hung dulux model aluminium windows and ventilators of approved make A.C.P/Pak cable including 6mm best thick quality tinted blue colour glass 12mm thick and aluminium fittings including wire mesh, lugs cutting holes and making good damages to wall etc. complete. Ornamented balustrade outside windows in entrance lobby and stores as per drawings floor or as directed by Engineer Incharge.
| Windows | 70 | Sft
| ventilators | 252 | Sft
C11 | Automatic sliding Doors
i) | Supply of Automatic Sliding Door Operator, complete with following electrical, mechanical components, and accessories. 1. High-strength reinforced fiber-toothed belt for quiet operation 2. heavy-duty track wheels (required quantity) 3. Presence Sensor 4. Safety Photo Beam for double leaf sliding glass doors. 5. Offered product should have international recognition for its quality / performance (verifiable). | 10 | Nos
ii) | Supply of Emergency Power Backup for Automatic Sliding Door Operator as per product requirement having backup capacity for minimum O5minutes/Open Close Operation. Installation, Testing and Commissioning of Automatic Sliding Door Operator with Emergency Power Backup as mentioned on above complete in all respect as per requirement. | 10 | Nos
C12 | S.S Railing
| Stainless Steel Railing (Stairs) Providing and fixing with sunken iron screws and rawal plugs best quality Stainless Steel Railing of seamless pipe rails and posts up to (3 inch dia) 7.5cm,100cm in height, both side of stairs and walls as required and approved by Engineer Incharge. | 32.55 | Rft
C13 | Basin
| Providing and fixing approved quality earthen ware glazed Wash basin standard size granite marble and approved colour master make. Chromium plated brass waste and Chain with rubber plug and CP mixture tap mixer heavy duty, bottle trap, complete with all fittings fixed to floor and walls by C.I. brackets with brass screws including C.P. stop cock complete in all respect. Or as approved equal. | 24 | No's
C14 | Door Lock
| Providing and fixing mortise door lock with handle and duplicate keys, made in Hungry (imported) or equivalent. | 52 | Nos.
C15 | Door Latches
| Providing and fixing best quality imported (Italian / German, available in Pakistan) door latches as per approval of Engineer Incharge | 52 | Nos.
C16 | Door Closer
| Providing and fixing with brass screws or specially supplied screws hydraulic Door Closer imported heavy-duty Ruby Make (Japan) medium size, complete as per specification | 40 | Nos.
C17 | Boxes
| Providing the Three pass Boxes (Static type) (as indicated in the design submitted). It shall be made of SS 304/416, with interlocking in such a way that both doors cannot be opened simultaneously, panel mounted, fixed at a height of 1220 mm from floor in sandwich panel, dimension of 610 mm (L) X 610 MM (W) X 610 MM (D), load bearing capacity of 40 Kg, door make-Single door in each side, glass and air tight gasket, door latch for one door(door opening outside), handle of superior quality, viewing glass made of polycarbonate or 10 mm thick tempered glass, hinges made of SS304 and chemical resistant especially to Hypochlorite solution, alcohol, etc., flange to seal pass-box and sandwich panel, | 3 | Nos.
C18 | Floor treament
| Flooring shall be of self-levelling industrial epoxy at least 3-5 mm in thick including screed compound for adhesion. Epoxy used for this application will be self-levelling and clean room compatible except laboratory office, staff room and kitchen. Floors must be slip-resistant, impervious to liquids, and resistant to chemicals. The installation of seamless, sealed, resilient or poured floors, with integral cove bases are required. Walls should be constructed to produce a sealed smooth finish that can be easily cleaned and decontaminated. All corners will be in curved shaped. | 15244.1189 | sft
C19 | Doors lock system
| Providing and fixing and installing high quality, durable electric door locks at Electric Locking Systems. We stock a variety of electric door locks to enhance the security. • Concealed installation • Power-on to lock, lock status LED display, Door status signal NC output • Working Voltage: DC12V input • Working Current: 350mA • Holding Force: 1000kg • Weight: 0.77kg • Size: 200×35×38mm | 10 | Nos.
C20 | Excavation & Back Filling For Tee Wall
| Excavation & Back Filling in all kinds of soil upto required depth and stacking of excavated material clear of edge of excavation, after excavation levelling and compacting and disposal of surplus excavated material out of project area any lead. Complete in all respects as per drawings, technical provisions and as directed by the Engineer In charge. | 2800.35 | Cft
C21 | Termite Proofing
| Providing and carrying out termite proofing by spraying anti-termite liquid as approved by Pakistan council of scientific and industrial research (PCSIR) lime BIFLEX, FIPROKIL AGENDA DURSBAN etc. as per instructions of the manufacturer, under floors over the filling and all peripheral sides of the trenches for foundation, and as directed by engineer Incharge. | 1400.175 | Sft
C22 | P.C.C (1:4:8)
| Providing, and laying cement concrete not leaner than (1:4:8) using screened Margalla crushed stone graded aggregate 1 inch (25 mm) and down gauge in foundations, having a minimum cylinder crushing strength of 10 Mpa (1500 psi) at 28 days under foundation including cost of 1000 gauge polythene sheet, form work and its removal, compacting, levelling and curing etc. as per drawings, technical provisions and instructions of the engineer Incharge | 200.025 | Cft
C23 | R.C.C for Tee Wall
Providing, and laying reinforced cement concrete using screened crushed stone graded aggregate 3/4 inch (19 mm) and down gauge having a minimum cylinder crushing strength of 5000 lbs. per sq inch at 28 days with including form work and its removal, compacting, levelling, and curing etc. complete in all respects but excluding the cost of reinforcement. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge
| Footing | 400.05 | Cft
| Columns | 509.3904 | Cft
| Beams | 509.3904 | Cft
C24 | Brick Work
| Providing and laying first class solid burnt brick masonry, set in cement morter 1:6 for brick work in straight or curved wall 9"thick including scaffolding and its removal, raking, out joints, and curing etc, complete in all respect and as directed by Engineer Incharge. | 2926.5705 | Cft
C25 | Plaster
| Providing 13mm thick cement plaster (1:4) on wall. including making edges, corners, curing, stagging, and scaffolding etc. Including cost of Providing and fixing chicken mesh with nails over all joints of walls with columns, beams, and footing bed. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 8301.0375 | Sft
C26 | Weather shied
| Painting three coats of weather shield paint (ICI/Burger/Nippon or approved equivalent) of approved shade on plastered surface (external) including projection soffits the cost of clearing the surface, sand papering etc. complete at any height in any floor.Complete in all respects as per darwings, technical provisions and as directed by the Engineer Incharge | 8001 | Sft
C27 | M.S Gate
| Providing and fixing of 16 gauge m.s folded sheet welded with angle box frame.2"x 2"x1/4" .M. s angle box frame with coats of red oxide and two coats of enamel paint including tower bolts, pull handle lock using approved brass section fittings, iron lugs, including cutting, welding. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 2 | Sft
C28 | Razor Wire
| Supply and fixing razor wire 12 No fencing consisting of 3no straight wire including fixing Y shape angle iron size (2"x2"x1/4'') with clamps or nut bolts at existing boundary wall column supports and razor wire, coil diameter of 24" at 6"c/c complete in all respects including cost of red oxide and paint on angles. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 472.25 | Rft
C29 | Reinforment
| Providing and laying M S Deformed grade 60 Steel reinforcement bars with minimum yield stress of 60,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, overlaps complete in all kinds of R.C.C work. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 1.1632 | Ton
C30 | Steel Elements of Truss
| Providing and fixing C Channel section (1.5"x3"x16 SWG) Box section 4" x 4" and 1/4" thickness, the Cleat 1/4" thickness, Base Plate 12"x12"x 1/2", Gusset 3/8" thickness and different size of Truss angle which is mentioned in drawing including the cost of straightening, cutting, bending, binding, wastage, overlaps. fixing material like nut bolt etc. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge. | 556 | Kg
C31 | Fiber Shed
| Providing, fabricating and fixing in position, galvanized corrugated G.I,18 SWG in thickness, including steel and rubber washer’s ‘J’ bolts and nuts including cost of material in over laps over roof sheeting and 18 SWG P.G.I sheet ridge cover, joints sealed of epoxy. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge. | 2224 | Sft
C32 | Emergancy M.S Doors
| Providing and fixing M.s Doors 16 SWG fixing material like nut bolt and inside the bar etc. With Iron Paint. Hatch doors Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge. | 320 | Sft
C33 | Window
| Providing and fixing of 16 gauge m.s folded sheet welded with angle box frame.2"x 2"x1/4" .M.s angle box frame with bullet Proof Glass 1" (25.4 mm) on With on glass shatter Resistance film SRF 12 mils (.012 inch )Thickness Place with adessive material with coats of red oxide and two coats of enamel paint including tower bolts, pull handle lock using approved brass section fittings, iron lugs, including cutting, welding. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge. | 531.216 | Sft
C34 | Window Grill
| Providing and fixing of M.S pipe grill frame with 3/4"x 3/4" x 16 SWG pipe and panel with 1/2" dia 18 SWG pipe for windows/ventilators including other maintenance and repair, cutting, welding, and painting as per design and drawings. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge. | 531.216 | Sft
C35 | M.S Sheet
| Providing and fixing of 16 SWG m.s folded sheet welded with angle box frame.2"x 2"x1/4" .M. s angle box frame with coats of red oxide and two coats of enamel paint including tower bolts, pull handle lock using approved brass section fittings, iron lugs, including cutting, welding. Complete in all respects as per drawings, technical provisions and as directed by the Engineer Incharge | 189 | Sft
C36 | M.s Sheet Cantainer
| Providing and install the M.s 16 SWG 20' Long container with two window and doors. One side window attaches the doors with Biometric device (scanner thumb and face) which for the external side Person communicate the outer side doors. The container fully installs of electric appliance, like CCTV Camera and AC facility. Complete in all respects as Engineer Incharge. | 1 | Jobs
C37 | Barrier Gate
| Providing and install Manual Barrier Gate with standard arm height (1052mm from road surface to the underside of the boom) Boom Dimensions (76mm x38mm) 7M boom with straining wire. | 1 | Job
C38 | Emergancy M.S stairs
| Providing and making, fixing the M.S stairs Emergency Stairs which through the connect all floor top to ground floor. The stairs all members should be M.s 16 SWG. Complete in all respects as Engineer Incharge. | 1 | Jobs
C39 | Metal Detectors
| Providing & Installing walk through metal detectors preferably Garret PD6500i Enhanced Pinpoint Walk-Through metal detector gate | 1 | Qty
Total Amount of Civil Works

## Electrical Works
Rehabilitation works for IOM-MHD Islamabad Office at Sector H/8, Islamabad
Ref # RFQ/PAK/May/2023 /040
BoQ’s for Electrical Works
S NO | DESCRIPTION | Qty | Unit | RATE(Rs) | AMOUNT(Rs)
Note:~ | The Contractor should note that materials and equipment as specified and as per list of Approved Manufacture/Make as Annexure-A1 (attached) shall be used.
E-01 | Supply, installation, testing & commissioning of circuit wiring from distribution board to the nearest switch board to be wired with 3xsingle core 2.5mm2 PVC insulated 300/500 volt grade copper wire (Phase Neutral & Earth) in and including cost of appropriate size of PVC conduit (min size 20mm dia) recessed in walls, columns, floors, slabs or as required as per site conditions complete with all PVC conduit accessories such as pull boxes, junctions boxes, sockets, bends, steel pull wire and complete in all respects. Each circuit shall have independent insulated green colour copper wire as earth conductor. | 105 | Each
Note: Not more than two circuits of the same phase in one conduit of 25mm dia.
Brands:
M/s Pakistan Cables (Pvt) Ltd Karachi, M/s Fast Cables (Pvt) Ltd, M/s GM Cables (Pvt) Ltd lahore or equivalent.
E-02 | 1-Light point Control by 1 Switch
| Wiring for one light point controlled by one switch and wired with 2x single core 1.5mm sq (7/053)/(3/036) PVC insulated, 300/500 volt grade copper wire (Phase, Neutral & Earth) in and including cost of appropriate size of PVC conduit (min size 20mm dia) partly shared recessed in walls, columns, floors, slabs or as required as per site conditions including all conduit accessories such as steel pull boxes, PVC junction boxes for ceiling and wall, sockets & bends also steel pull wire. Complete in all respects with final testing and commissioning. | 65 | Points
Same as item E-02 mentioned above but set of light points controlled by one switch as under:-
| a. Two Light Points | 304 | Points
E-03 | 1-Light Point Control by 2 way Switch
| Same as item E-02 mentioned above but one light point controlled by 2-two way switches as shown in the drawings. | 10 | Points
E-04 | Exhaust Fan Points
| Same as item E-02 mentioned above but for Exhaust fan. | 16 | Each
E-05 | 3 Pin 13 AMPS Switch Sockets
| Same as item E-02 mentioned above but wiring for 3 pin 13 AMP switch socket combined unit but with 3x single core 2.5mm Sq (7/029) from nearest switch board. Complete in all respect with final testing and commissioning. | 220 | Each
E-06 | 3 Pin 15 AMPS Switch Sockets
| Supply, installation, testing & commissioning of circuit wiring from distribution board to the nearest socket/plug to be wired with 3xsingle core 4mm2 PVC insulated 300/500 volt grade copper wire (Phase Neutral & Earth) in and including cost of appropriate size of PVC conduit (min size 20mm dia) recessed in walls, columns, floors, slabs or as required as per site conditions complete with all PVC conduit accessories such as pull boxes, junctions boxes, sockets, bends, steel pull wire and complete in all respects. Each circuit shall have independent insulated green colour copper wire as earth conductor. | 98 | Each
E-07 | 3 Pin 15 AMPS Switch Sockets (AC Socket)
| Wiring for one 3 pin 15 AMP switch-socket combined unit direct from DB with 3xsingle core 4mm sq (7/036) PVC insulated, 300/500 volt grade copper wire (Phase, Neutral & Earth) in and including cost of 25mm dia PVC conduit recessed in walls, columns, floors, slabs or as required as per site condition including all conduit accessories such as sockets, bends, steel pull boxes and complete in all respects with final testing and commissioning. | 60 | Each
E-07A | 32 AMPS Sockets
Socket Wiring For 3 Phase
| Wiring for one 5 pin 32 AMP switch-socket combined unit direct from main panel with 5xsingle core 4 mm sq PVC insulated, 300/500 volt grade copper wire (Phase, Neutral & Earth) in and including cost of 25/40mm dia PVC conduit recessed in walls, columns, floors, slabs or as required as per site condition including all conduit accessories such as sockets, bends, steel pull boxes and complete in all respects with final testing and commissioning. | 20 | Each
E-08 | Supply and installation of 10 amps switch gang plate with appropriate size of back steel box 16SWG with earth terminal, two coats of antirust paint fixed recessed in wall including all fixing accessories and of following types:
| i) 1 gang switch plate | 5 | Each
| ii) 2 gang switch plate | 45 | Each
| iii) 3 gang switch plate | 20 | Each
| iii) 4 gang switch plate | 10 | Each
| iv) 5 gang switch plate | 7 | Each
| v) 6 gang switch plate | 5 | Each
E-09 | Same as item E-01 mentioned above but two-way gang switch plate of following types:-
| i) 1-gang switch plate | 10 | Each
E-10 | Supply and installation of 3 pin switch socket combined unit with appropriate size of back steel box 16SWG, two coats of antirust paint, fixed recessed to walls or ceiling including all fixing accessories and of the following types:-
| ii) 3 pin 13 Amps switch socket unit | 196 | Each
| iii) 3 pin 15 Amps switch Twin socket unit | 60 | Each
| iv) 5 pin 32 Amps industerial switch socket unit | 20 | Each
Brands for Switches, Plugs, Hum Free Regulator & Accessories:
Schenider, Clipsal, Legrand or equivalent
Brands for Cable and Wires:
M/s Pakistan Cables (Pvt) Ltd Karachi, M/s Fast Cables (Pvt) Ltd, M/s GM Cables (Pvt) Ltd lahore or equivalent.
E-11 | Supply, Installation, testing and commissioning of following light fittings, ceiling, wall mounted Complete with LED Drivers, internal wiring, earthing terminal complete in all respects and duly approved by Engineer-in-Charge and of following types:
i) | LED Surface Mounted down light, 16 watts 220/240 volts, round approved type Standard, Supply and fixing | 603 | Each
ii) | Bulk Head Light 20W IP-65 220/240 volts for wall or ceiling mounted approved type Standard, Supply and fixing. | 19 | Each
iii) | LED Mirror light ,16 watt 220/240 volts for wall or ceiling mounted approved type Standard, Supply and fixing. | 20 | Each
iv) | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp starter, electronic ballast & capacitor as Philips Cat. (TMS- 015/236) | 20 | Each
Brands Lightning Fixtures:
M/s Signify (Philips), M/s NVC, M/s Osram, M/s Opple or equivalent.
E-12 | Providing & installing 30 Cm ( 12") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal.
| i)12" dia | 18 | Each
Brands for Fans & Dimmer:
Royal, Pak Fan, Climax, Lahore Fans, GFC and equivalent
E-13 | Supply, installation, testing and commissioning of single core, stranded copper conductor, PVC insulated, 450/750 volt grade in pre-laid conduits/trenches or on cable trays as per route shown on drawings or as directed by Engineer-in-Charge including cost of all necessary materials, termination, cable lugs properly crimped at both ends and of the following sizes and of the following sizes:-
a) | a) Single Core, PVC insulated Copper Cable
| i) 1 core 4mm sq + 1 x 2.5mm sq as ECC | 120 | Meter
| ii) 1 core 6mm sq + 1 x 4mm sq as ECC | 100 | Meter
| iii) 1 core 10mm sq + 1 x 6mm sq as ECC | 80 | Meter
| iv) 1 core 16mm sq + 1 x 10mm sq as ECC | 70 | Meter
b) | b) Multicore, PVC insulated & PVC Sheathed
| i) 4 core 70mm sq + 1 x 6 mm sq as ECC | 70 | Meter
| ii) 4 core 4mmsq + 1 x4 mm sq as ECC | 100 | Meter
| iii) 4 core 16mmsq + 1 x4 mm sq as ECC | 100 | Meter
| iv) 4core 35mmsq + 1 x6 mm sq as ECC | 80 | Meter
c) | c) Single Core, LT XLPE Copper Cable
| i) 3x4 Core 185 mm sq + 1x120 mm sq as ECC | 50 | Meter
E-14 | Supply, installation, testing of PVC conduit as specified concealed in RCC slabs, walls, floors columns or fixed to slab, wall above false ceiling as per site conditions including cost of all conduit accessories, steel pull boxes, pull wire, junction boxes and complete in all respects and of the following sizes:
| c) 1¼ " dia | 5197 | Rft
| d) 1½ " dia | 250 | Rft
| e) 2" dia | 250 | Rft
Note: Contractor will carryout measurement as per shop drawing approved and will forward the same prior to purchase and installation for approval of Engineer-in-Charge.
E-15 | Supply, installation, testing and commissioning of factory fabricated distribution boards for light/power, concealed type made of M.S sheet 16 SWG degreased, derusted, zinc phosphated finished with electrostatic powder coating, of approved colour with hinged door, lockable handle, protection plate, earth and neutral strip, complete internally wired, flexible earthing strap for door manufactured by any one of the approved manufacturers as specified and comprising as under:
Brands for Cable and Wires:
M/s Pakistan Cables (Pvt) Ltd Karachi, M/s Fast Cables (Pvt) Ltd, M/s GM Cables (Pvt) Ltd lahore or equivalent.
Brands for PVC Conduits & Accessories:
Dadex, Beta, Popular, Adamjee, GM Pipes or equivalent.
E16 | a. Main Panel | 1 | Nos
| Providing & fixing cubical type metal sheet vermin protected LT panel board as per drawing with locking arrangement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 50 | P/Sft
INCOMING
1x500AMP, FP, MCCB,
| Providing & fixing 400 to 630 Amps,( High Breaking Capacity) T.P circuit breaker fixed on existing board , I/c inter-connection as required. | 1 | Each
| Providing & fixing 300 Amps, 4 pole, three phase bus bar strip set (Standard size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each
| Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 1 | Set
| Providing & fixing rotary type, 63/50 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 1 | Each
| Volt Meter 96mm x 96mm | 1 | Each
| Ampere Meter 96mm x 96mm CT operated 150 to 1000 Amp | 1 | Each
| Current transformer 600/5 Amp | 1 | Each
Indication Lights Red, Yellow, Green
OUTGOING
| 3x20AMP, TP, MCCB, 30KA with O/L & S/C Protection. | 3 | Each
Providing & fixing 10 to 60 Amps,( High Breaking Capacity) T.P MCCB fixed on existing board , I/c inter-connection as required.
| 1x50AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 1 | Each
Providing & fixing 10 to 60 Amps,( High Breaking Capacity) T.P MCCB fixed on existing board , I/c inter-connection as required.
| 2x120AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 2 | Each
120-225 Amps TP MCCB Amps (High Breaking Capacity)
| 1x150AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 1 | Each
120-225 Amps TP MCCB Amps (High Breaking Capacity)
SPARE Circuit Breaker
| 1x20AMP, TP, MCCB, 30KA with O/L & S/C Protection. | 1 | Each
| 1x50AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 1 | Each
| 1x120AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 1 | Each
| 1x150AMP, TP, MCCB, 15KA with O/L & S/C Protection. | 1 | Each
Indication Lights Red, Yellow, Green
Distribution Board (DBS)
| LDB-BF | 1 | Nos
INCOMING
1x20AMP, TP, MCCB, 6KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
14x6AMP, SP, MCB.
SPARE Circuit Breaker
03x6AMP, SP, MCB.
| PDB-BF | 1 | Nos
INCOMING
1x130AMP, TP, MCCB, 36KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
30x16AMP, SP, MCB.
3x50AMP, SP, MCCB.
SPARE Circuit Breaker
5x16AMP, SP, MCB.
1x50AMP, SP, MCCB.
Distribution Board (DBS)
| LDB-GF | 1 | Nos
INCOMING
1x20AMP, TP, MCCB, 6KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
14x6AMP, SP, MCB.
SPARE Circuit Breaker
03x6AMP, SP, MCB.
| PDB-GF | 1 | Nos
INCOMING
1x120AMP, TP, MCCB, 36KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
24x16AMP, SP, MCB.
8x50AMP, SP, MCCB.
SPARE Circuit Breaker
5x16AMP, SP, MCB.
2x50AMP, SP, MCCB.
| LDB-FF | 1 | Nos
INCOMING
1x20AMP, TP, MCCB, 6KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
18x6AMP, SP, MCB.
SPARE Circuit Breaker
03x6AMP, SP, MCB.
| PDB-FF | 1 | Nos
INCOMING
1x120AMP, TP, MCCB, 36KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
37x16AMP, SP, MCB.
SPARE Circuit Breaker
6x16AMP, SP, MCB.
| LDB-SPARE FOR ROOMS (ALL ROOMS) | 1 | Nos
INCOMING
1x10AMP, TP, MCCB, 6KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
2x6AMP, SP, MCB.
SPARE Circuit Breaker
01x6AMP, SP, MCB.
| DB-LAB | 1
INCOMING
1x50AMP, TP, MCCB, 15KA
Digital Voltmeter With Selector Switch
Indication Lights Red, Yellow, Green
OUTGOING
05x6AMP, SP, MCB.
15x16AMP, SP, MCB.
SPARE Circuit Breaker
01x6AMP, SP, MCB.
03x16AMP, SP, MCB.
Brands for Sub-Main Panel Boards, distribution Boards, Rising Mains, Bus - Tie Duct
M/s ELECTRECH, M/s ERCON, M/s Capital Electro, M/s Bilal Switchgear, M/s South Asian Electric Concerns, M/s Power Tech Switchgear Services, M/s Ravi Switchgear (Pvt) Ltd or equivalent.
Earthing Pit for Equipments
E-17 | Constructing, erecting, earthing pit including cost of excavation and back filling of the earth pit upto 3500 to 4500mm depth and including electrode comprising of one 16 mm dia earth electrode rod of 3600 mm long with loop conductor as bare copper conductor 70 mm2 to be drawn in 40mm dia uPVC sleeves from copper plate (50x200 mm) to earth terminal point or adjacent earthing pit or direct to equipment (as directed by Engineer-in-Charge) complete with thimbles, brass nuts and bolts for fastening earth conductor and also including constructing inspection pit 450mm x 450mm x 200mm with RCC cover complete with all necessary materials complete in all respects as per detail shown in the drawing with final testing and commissioning including the cost of earthing leads. | 10 | Each
Brands for Earthing Pit for Equipments:
Earthlinks Pakistan, Techno Power Engineering (Pvt) Ltd or equivalent.
E-18 | LIGHTENING PROTECTION SYSTEM
| Supply, installation, testing & commissioning of Air Terminals (16mm Dia 36"long) copper rod with base and all accessories required for installation, as approved by the engineer in charge. (As per Early Streamer Emission (ESE) Type Lightning Protection System) | 1 | Job
| Supply and laying of 70 mm x 3mm Cu Strip condutor as down conductor to be connected to earthing pit. including cost of all necessary material | 210 | Rft
Brands for Lightning Protection System:
Earthlinks Pakistan, Techno Power Engineering (Pvt) Ltd or equivalent.
Earthing Pit
| Constructing, erecting, earthing pit including cost of excavation and back filling of the earth pit upto 3500 to 4500mm depth and including electrode comprising of one 16 mm dia earth electrode rod of 3600 mm long with loop conductor as bare copper conductor 70 mm2 to be drawn in 40mm dia uPVC sleeves from copper plate (50x200 mm) to earth terminal point or adjacent earthing pit or direct to equipment (as directed by Engineer-in-Charge) complete with thimbles, brass nuts and bolts for fastening earth conductor and also including constructing inspection pit 450mm x 450mm x 200mm with RCC cover complete with all necessary materials complete in all respects as per detail shown in the drawing with final testing and commissioning including the cost of earthing leads. | 2 | Each
Earth Loop Conductor
Providing and laying earth loop conductor complete with fixing, arrangement from one earthing pit to another earthing pit with lugs and thimbles, washers and of the following sizes:
| a. Bare copper conductor 70mm sq | 100 | Rft
Brands for Earthing Pit for Equipments:
Earthlinks Pakistan, Techno Power Engineering (Pvt) Ltd or equivalent.
PUBLIC ADDRESS SYSTEM
E-19 | Wiring for speakers with 2x1.5 mm2 shielded stranded copper wire including cost of appropriate size of PVC 1 inch conduit shown in drawings and as approved by Engineer in charge. | 20 | Points
1 | Supply, installation of Remote Microphone as approved by Engineer in charge. | 1 | Nos
2 | Supply, installation of Ceiling Mounted Speaker 6W with tap settings (8 ohm) with complete auxilliaries shown in drawings and as approved by Engineer in charge. | 20 | Nos
3 | Supply, installation of Terminal Board (10 terminals) complete with auxiliaries and as approved by Engineer in charge. | 5 | Nos
4 | Supply, installation of Main Amplifier Ruck 600 Watt 4 zone selector with CD player complete with all auxiliaries and as approved by Engineer in charge. | 1 | Nos
Brands For Public Address System:
TOTAL Amount of Electrical Works

## Fire Life Safety
Rehabilitation works for IOM-MHD Islamabad Office at Sector H/8, Islamabad
Ref # RFQ/PAK/May/2023 /040
BoQ’s for Engineering Fire Life Safety
SR.No. | DESCRIPTION | Qty | UNIT | Rate (Rs) | AMOUNT (Rs)
1 | FACP : Providing and fixing, testing and commissioningof 02 loop analogue fire control panel surface /recessed mounting type with full switching programming capabilities ,system suitable operation of 230 volts 50hz with full functionality as per specification of manufacturer allied components. with T&P etc and as per specific drawing imported approved make /model or as approved by the engineer in-charge as required. | 1 | No
2 | SMOKE DETECTOR : Providing and fixing, testing and commissioning of analogue addressable ionization smoke detector with addressable base with full functioning switching programming capabilities ,system as per specification & recommended of drawing / manufacturer with allied components with T&P etc imported approved make/model or as approved by the engineer in-charge as required. | 72 | No
3 | MANUAL BREAK GLASS:Providing and fixing, testing and commissioning o addressable manual brake glass unit with addressable base with full functioning switching programming capabilities ,system as per specification & recommended of drawing / manufacturer with allied components with T&P etc imported approved make/model or as approved by the engineer in-charge as required. | 11 | No
4 | SOUNDER:Providing and fixing, testing and commissioning of addressable electronic sounder unit with addressable base with full functioning switching programming capabilities ,system as per specification & recommended of drawing / manufacturer with allied components with T&P etc approved make/model or as approved by the engineer in-charge as required. | 11 | No
5 | Wiring for Fire alarm system with 2 Core 1.5mmSq Fire Rated PVC insulated copper wire make as specified from FACP/FAJB includings cost of PVC conduit partly shared. Complete in all respects including no. of wires as per standard practice and shop drawings approved by Engineer-in-Charge. Excluding cost of smoke/heat detectors as per NFPA-72 requirement. | 335 | M
6 | EMERGENCY LIGHT:Supply and installation of Emergency Light with 1.5 Hours beak up (Battery Operated) for electrical room as per drawing and as per NFPA 101, 70, 110, 111 & ISO, IBC 1006-2, UL 924 requirements. | 56 | No
7 | RESCUE BOX:Supply and fixing of Rescue Boxes as per drawing & NFPA relevent code requirements. | 4 | No
8 | CO2 EXTINGUISHER:Supplying, installingand commissioning of CO2 make fire Extinguisher containing Mono Ammonium Phosphate Powder 50, Stored Pressure Type, Pressure Gauge, fittted with discharge hose, wall mounting bracket etc., Discharge Time less than 15 Secs, Controllable discharge mechanism, Range minimum 4 Meters, applicable on Class A,B,C and electrically started Fire, A Rating- 8A, B Rating 34B, Can Construction : Deep drawn & Co2 Mig welded, Valve Construction : Forging & Machining, Internal Coating of Can : Epoxy Powder coating, External Coating of Can : Epoxy Polyster Powder coating, Sheet metal thickness : 1.60MM, ISI approved as per IS:15683:2006 | 19 | No
9 | DCP EXTINGUISHER 6 KG:Supplying, installing and commissioning of portable Fire Extinguisher containing 6 kg (Dry chemical) Stored Pressure Type, Pressure Gauge, fittted with discharge hose, wall mounting bracket etc., Discharge Time less than 15 Secs, Controllable discharge mechanism, Range minimum 4 Meters, applicable on Class A,B,C and electrically started Fire, A Rating- 8A, B Rating 34B, Can Construction : Deep drawn & Co2 Mig welded, Valve Construction : Forging & Machining, Internal Coating of Can : Epoxy Powder coating, External Coating of Can : Epoxy Polyster Powder coating, Sheet metal thickness : 1.60MM, ISI approved as per IS:15683:2006 | 19 | No
10 | WET CHEMICAL EXTINGUISHER:Supplying, installing , testing and commissioning of wet chemical fire extinguisher 6 Kg as per drawing. | 2 | No
11 | FIRE BLANKET:Supply, installation, testing and commissioning of fire blanket as per drawing. | 10 | No
13 | FIRE HOSE REEL:Providing and fixing first aid hose reel full swinging type with 30 meter long 20mm dia rubber lined Maruti pipe with shut off nozzle of 5 mm dia, house reel wiht all sockets, nipples, elbows and ball valve as per drawing complete with all necessary fittings and requirements as per NFPA-14 | 4 | No
14 | FIRE PUMP:Supply, fixing, testing and commissioning of Firefighting pump 900 LPM, NAFFCO or SAFFCO made, with base frame and all accessories complete with all necessary fittings FM/UL approved and requirements as per NFPA-20 requirements. | 1 | No
15 | MS. SEAMLESS PIPE:Supply and Installation of epoxy painted seamless MS steel pipe schedule 40.According to ASTM-A 53 / ASTM A 106, ISO standard 9001, 14001, OHSAS 18001 for firefighting water, medium weight, including all fittigns, brackets, flanges, tees, expansion devices, hanger's. Note: IIL MS 40 or equilent pipe
16 | 4" DIA | 40 | RFT
| 2.5" DIA | 253 | RFT
| 2" DIA | 18 | RFT
| 1-1/2" DIA | 22 | RFT
| 1-1/4" DIA | 20 | RFT
| 1"DIA | 231 | RFT
17 | NON RETURN VALVE:Supplying, installing, testing and commissioning of Swing NRV flanged as per BS with required flange, nuts, bolts etc. complete in all respect and as per direction of Engineer incharge.According to NFPA-25 & NFPA-69 compliance. | 1 | No
18 | 4" Dia
19 | EXIT DIRECTION SIGN:Supply, installation in position of the signage Fire Exit signage at each stair on every floor, indicating the direction of fire exit, lettering size shall be 7.5 cm with contrasting color from back ground BS 5499, ISO 7010, BS-EN-60598-2-22 (1998) luminaire. | 21 | No
20 | EXIT SIGN:Supply, installation in position of the signage Fire Exit door signage at each floor, indicating the direction of Fire Exit door (in case of fire) , lettering size shall be 7.5cm with contrasting color from background . Size shall be 9" height x 9" width as per BS 5499 requirements. | 14 | No
21 | ASSEMBLY POINT:Supply, installation in position of the signage fire assembly point signage at each floor, indicating the direction of fire assembly point (in case of fire) , lettering size shall be 7.5cm with contrasting color from back ground. Size shall be 9" height x 9" width & as per BS 5499 code requirement. | 1 | No
22 | FIRE EQUIPMENT SIGN:Supply, installation in position of the signage Firefighting equipment location signage at each floor, indicating the direction ofFirefighting equipment location sign (in case of fire) , lettering size shall be 7.5cm with contrasting color from back ground. Size shall be 9" height x 9" width acrylic plate, silk-screened printing & as per BS 5499 code requirement. | 23 | No
23 | PROHIBITION SIGN:Supply, installation in position of the signage Prohibition signage at each floor, indicating the Prohibition sign (in case of fire) , lettering size shall be 7.5cm with contrasting color from back ground. Size shall be 9" height x 9" width as per BS 5499 code requirement. | 7 | No
24 | NON SLIPPERY STRIPS: Supply , installationof nos slippery strips as per drawing and as per NFPA standard. | 212 | NO
25 | FIRE RATED DOOR(2hr FRD):Imported, China Made Hollow metal fire rated doors as per NFPA spacification for stability and integrity. Pressed Galvanized steel confirming to NFPA with specification. Certified UL/FM and ISO 9001 certified fire door shall have tested at Local and International labs for maximum rating of 2hrs with non vision panel. Test certificates should be available for panels as part of the fire door assembly. Manufacturer test certificate shall cover doors both single and double leaf and all doors supplied should be within the tested specimen, deviation in specification and sheet thickness other than what is mentioned in the test certificates are not allowed. Proper label confirming the type of door and the hourly rating is mandatory. | 1 | NO
26 | CEILING MOUNTED AUTO DCP 6 KG:Supplying, installing and commissioning of 6 kg ceiling mounted auto CO2 fire Extinguisher as per drawings and NFPA-10 Standard. | 7 | NOS
27 | SHATTER RESISTANT FILM:Supplying and installing of shatter resistant film on glass as per drawings | 1900 | SFT
TOTAL Amount of Engineering Fire Life Safety

## HVAC
Rehabilitation works for IOM-MHD Islamabad Office at Sector H/8, Islamabad
Ref # RFQ/PAK/May/2023 /040
BoQ’s for HVAC Engineers
SR.No. | DESCRIPTION | Qty | UNIT | Rate (Rs) | AMOUNT (Rs)
1 | Providing, installation, testing commissioning of Copper Refrigerant Piping to be connected without door. The copper piping shall include, liquid, suction line, the copper piping shall be further covered with foam insulation complete in all respects. | 130 | Rft
2 | Providing & Installation of High Efficiency Particulate Air (Filter>99.999% at 0.1 to 0.3 micron, ULPA as per IEST-RP-CC001.3 USA >99.999% at MPPS, H14 as per EN 1822 EU>99.99% on 0.3 micron size particles by PAO test (filter leakage test according to NSF49)) in the separate exhaust (709 cmh (417 cfm)) inside the laboratory with damper, two exhaust independently operated by the laboratory connected with PVC pipes B class or higher (10-12 inches ) The exhaust/blowers should be weather proofed to prevent water, wildlife and wind/dust damage, and covered with a grille. The laboratory shall be designed such that the airflow will not be reversed under failure conditions with anti-blowback valve and exhaust dampers | 2 | Nos
APPROVED MANUFACTURER: MULLER /TROX OR EQUIVALENT
3 | Providing, fabrication, installation of Galvanized Iron Sheet Metal Ducting with insulation, fittings like elbows, tees, reducers, splitter dampers, complete with hangers, supports inserts etc. as shown in the drawings complete in all respects as per drawings, specification and as approved by the Consultant | 2800 | Sft
APPROVED MANUFACTURER, Ayesha steel, Pakistan Steel OR EQUIVALENT
4 | Providing, installation of Duct Flexible Connector with all ducts connecting to rotating equipment like air handling units, exhaust fans etc. complete in all respects as per drawings & specifications and as approved by the Consultant. | 200 | Rft
APPROVED MANUFACTURER Ductmate/Durodyne/or approved equivalent
5 | Providing, installation, of Air Devices made with extruded aluminium section complete in all respects as per drawings, specification and as approved by the Consultant. Damper, Diffusers, Grills, Louvers, VCDs
| Exhaust grill | 22 | Nos
| Fire damper | 26 | Nos
APPROVED MANUFACTURER, Steel Craft/Carrier Engg. /Or approved equivalent
6 | Supply, Installation, Testing and Commissioning of Indoor Units suitable for VRF / VRV System.
| Cassette Unit 1.5 ton | 5 | Ton
| Cassette Unit 2 ton | 17 | Ton
| Split Ac Unit 1.5 ton | 40 | Ton
| Split Ac Unit 2 ton | 9 | Ton
| Split Ac Unit 2.5 ton | 1 | Ton
APPROVED MANUFACTURER Any Manufacturer of Origin USA, JAPAN, EUROPE, THAILAND
7 | Drain piping in hard pvc with all fittings, supports and clamps upto 80 mm dia, including drilling hole in wall chipping wall etc to conceal and to route the drainpipe. The piping shall be suitably insulated with 19mm thick closed cell foam insulation class o stuck with approved adhesive compound. the insulation shall be covered with glass cloth and painted with rubberised paint. | 1005 | Rft
8 | supply, Installation, Testing and Commissioning of y joints for the connections of copper pipes, as per drawing and with the approval of Engineer Incharge. | 64 | Nos
APPROVED MANUFACTURER MULLER /TROX OR EQUIVALENT
9 | Ducted Fans (To be installed in Existing Toilet Extract Ducts with suitable duct modifications). Pantry fans to be hooked up to Developer's duct. Fans shall be of Low noise. Selection to be approved by consultant. Fans to be inserted in existing ducting provided by the developer with suitable mounted arrangement and with back draft damper. | 14 | Nos
APPROVED MANUFACTURER Pak Gfans, GFC fans
10 | Ducted Fans to be installed at top roof that serve all the floor for exhaust... Fans shall be of Low noise. Selection to be approved by consultant. Fans must be equipped with back draft damper.
| 4500 CFM fan | 1 | Nos
| 2000 CFM | 1 | Nos
APPROVED MANUFACTURER Any Manufacturer of Origin USA, JAPAN, EUROPE, THAILAND
TOTAL Amount of HVAC Engineering